## table1
Table 1
Class 1 Solid conductors for single-core and multicore cables
1 | 2 | 3 | 4
Nominal cross-sectional area | Maximum resistance of conductor at 20degC/km
| Circular copper conductors |  | Aluminium conductors circular or shaped, plain, metal-coated or metal-clad
| Plain | Metal-coated
0.5 | 36 | 36.7 | -
0.75 | 24.5 | 24.8 | -
1 | 18.1 | 18.2 | -
1.5 | 12.1 | 12.2 | 18.1
2.5 | 7.41 | 7.56 | 12.1
4 | 4.61 | 4.7 | 7.41
6 | 3.08 | 3.11 | 4.61
10 | 1.83 | 1.84 | 3.08
16 | 1.15 | 1.16 | 1.91
25 | 0.727 | - | 1.2
35 | 0.524 | - | 0.868
50 | 0.387 | - | 0.641
70 | 0.268 | - | 0.443
95 | 0.193 | - | 0.32
120 | 0.153 | - | 0.253
150 | 0.124 | - | 0.206
185 | - | - | 0.164
240 | - | - | 0.125
300 | - | - | 0.1

## table2
Table 2
Class 2 Stranded conductors for single-core and multicore cables
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Nominal Cross Section Area | Minimum number of wires in the conductor | [5 empty] | Maximum resistance of conductor at 20degC/km
| Circular conductor (non-compacted) |  | Circular compacted conductor |  | Shaped conductor |  | Copper conductor |  | Aluminium conductor, plain, metal-coated or metal-clad wires
| Cu | Al | Cu | Al | Cu | Al | Plain wires | Metal-coated wires
0.5 | 7 | - | - | - | - | - | 36 | 36.7 | -
0.75 | 7 | - | - | - | - | - | 24.5 | 24.8 | -
1 | 7 | - | - | - | - | - | 18.1 | 18.2 | -
1.5 | 7 | - | 6 | - | - | - | 12.1 | 12.2 | -
2.5 | 7 | - | 6 | - | - | - | 7.41 | 7.56 | -
4 | 7 | 7 | 6 | - | - | - | 4.61 | 4.7 | 7.41
6 | 7 | 7 | 6 | - | - | - | 3.08 | 3.11 | 4.61
10 | 7 | 7 | 6 | - | - | - | 1.83 | 1.84 | 3.08
16 | 7 | 7 | 6 | 6 | - | - | 1.15 | 1.16 | 1.91
25 | 7 | 7 | 6 | 6 | 6 | 6 | 0.727 | 0.734 | 1.2
35 | 7 | 7 | 6 | 6 | 6 | 6 | 0.524 | 0.529 | 0.868
50 | 19 | 19 | 6 | 6 | 6 | 6 | 0.387 | 0.391 | 0.641
70 | 19 | 19 | 12 | 12 | 12 | 12 | 0.268 | 0.27 | 0.443
95 | 19 | 19 | 15 | 15 | 15 | 15 | 0.193 | 0.195 | 0.32
120 | 37 | 37 | 18 | 18 | 18 | 15 | 0.153 | 0.154 | 0.253
150 | 37 | 37 | 18 | 18 | 18 | 15 | 0.124 | 0.126 | 0.206
185 | 37 | 37 | 30 | 30 | 30 | 30 | 0.0991 | 0.1 | 0.164
240 | 61 | 61 | 34 | 34 | 34 | 30 | 0.0754 | 0.0762 | 0.125
300 | 61 | 61 | 34 | 34 | 34 | 30 | 0.0601 | 0.0607 | 0.1
400 | 61 | 61 | 53 | 53 | 53 | 53 | 0.047 | 0.0475 | 0.0778
500 | 61 | 61 | 53 | 53 | 53 | 53 | 0.0366 | 0.0369 | 0.0605
630 | 91 | 91 | 53 | 53 | 53 | 53 | 0.0283 | 0.0286 | 0.0469
800 | 91 | 91 | 53 | 53 | - | - | 0.0221 | 0.0224 | 0.0367
1000 | 91 | 91 | 53 | 53 | - | - | 0.0176 | 0.0177 | 0.0291
1200 | 1) | 1) | 1) | 1) | - | - | 0.0151 | 0.0151 | 0.0247
1400 | 1) | 1) | 1) | 1) | - | - | 0.0129 | 0.0129 | 0.0212
1600 | 1) | 1) | 1) | 1) | - | - | 0.0113 | 0.0113 | 0.0186
1800 | 1) | 1) | 1) | 1) | - | - | 0.0101 | 0.0101 | 0.0165
2000 | 1) | 1) | 1) | 1) | - | - | 0.009 | 0.009 | 0.0149

## table3
Table 3
Class 5 Flexible copper conductors for single-core and multicor cables
1 | 2 | 3 | 4
Nominal Cross Section Area | Maximum diameter of wires in conductor | Maximum resistance of conductor at 20degC/km
|  | Plain wires | Metal-coated wires
0.5 | 0.21 | 39 | 40.1
0.75 | 0.21 | 26 | 26.7
1 | 0.21 | 19.5 | 20
1.5 | 0.26 | 13.3 | 13.7
2.5 | 0.26 | 7.98 | 8.21
4 | 0.31 | 4.95 | 5.09
6 | 0.31 | 3.3 | 3.39
10 | 0.41 | 1.91 | 1.95
16 | 0.41 | 1.21 | 1.24
25 | 0.41 | 0.78 | 0.795
35 | 0.41 | 0.554 | 0.565
50 | 0.41 | 0.386 | 0.393
70 | 0.51 | 0.272 | 0.277
95 | 0.51 | 0.206 | 0.21
120 | 0.51 | 0.161 | 0.164
150 | 0.51 | 0.129 | 0.132
185 | 0.51 | 0.106 | 0.108
240 | 0.51 | 0.0801 | 0.0817
300 | 0.51 | 0.0641 | 0.0654
400 | 0.51 | 0.0486 | 0.0495
500 | 0.61 | 0.0384 | 0.0391
630 | 0.61 | 0.0287 | 0.0292

## table4
Table 4
Class 6 Flexible copper conductors for single-core and multicor cables
1 | 2 | 3 | 4
Nominal Cross Section Area | Maximum diameter of wires in conductor | Maximum resistance of conductor at 20degC/km
|  | Plain wires | Metal-coated wires
0.5 | 0.16 | 39 | 40.1
0.75 | 0.16 | 26 | 26.7
1 | 0.16 | 19.5 | 20
1.5 | 0.16 | 13.3 | 13.7
2.5 | 0.16 | 7.98 | 8.21
4 | 0.16 | 4.95 | 5.09
6 | 0.21 | 3.3 | 3.39
10 | 0.21 | 1.91 | 1.95
16 | 0.21 | 1.21 | 1.24
25 | 0.21 | 0.78 | 0.795
35 | 0.21 | 0.554 | 0.565
50 | 0.31 | 0.386 | 0.393
70 | 0.31 | 0.272 | 0.277
95 | 0.31 | 0.206 | 0.21
120 | 0.31 | 0.161 | 0.164
150 | 0.31 | 0.129 | 0.132
185 | 0.41 | 0.106 | 0.108
240 | 0.41 | 0.0801 | 0.0817
300 | 0.41 | 0.0641 | 0.0654

## table5
Table 5
Temperature correction factor k for conductor resistance to correct the measured resistance at t degC to 20degC
Temperature of conductor at time of measurement | Correction factor
5 | 1.064
6 | 1.059
7 | 1.055
8 | 1.05
9 | 1.046
10 | 1.042
11 | 1.037
12 | 1.033
13 | 1.029
14 | 1.025
15 | 1.02
16 | 1.016
17 | 1.012
18 | 1.008
19 | 1.004
20 | 1
21 | 0.996
22 | 0.992
23 | 0.988
24 | 0.984
25 | 0.98
26 | 0.977
27 | 0.973
28 | 0.969
29 | 0.965
30 | 0.962