## table1
Table 1
Electrical resistivities and temperature coefficients of metals used
Material |  | Resistivity ohm-m at 20degC | Temperature coefficient per K at 20degC
a - Conductors | Copper | 1.7241e-08 | 0.00393
| Aluminium | 2.8264e-08 | 0.00403
b - Sheaths and armour | Lead or lead alloy | 2.14e-07 | 0.004
| Steel | 1.38e-07 | 0.0045
| Bronze | 3.5e-08 | 0.003
| Stainless Steel | 7e-07 | 0.001
| Aluminium | 2.84e-08 | 0.00403

## table2
Table 2
Experimental values for the coefficients ks and kp
Type of conductor |  | Conductor insulation system | ks | kp
Copper | Round, solid | All | 1 | 1
| Round, stranded | Fluid/paper/PPL | 1 | 0.8
| Round, stranded | Extruded/Mineral | 1 | 1
| Round, Milliken | Fluid/paper/PPL | 0.435 | 0.37
| Round, Milliken, insulated wires | Extruded | 0.35 | 0.2
| Round, Milliken, bare uni-directional wires | Extruded | 0.62 | 0.37
| Round, Milliken, bare uni-birectional wires | Extruded | 0.8 | 0.37
| Hollow, helical stranded | All | a | 0.8
| Sector-shaped | Fluid/paper/ppl | 1 | 0.8
| Sector-shaped | Extruded/Mineral | 1 | 1
Aluminium | Round, solid | All | 1 | 1
| Round, stranded | All | 1 | 0.8
| Round, Milliken | All | 0.25 | 0.15
| Hollow, helical stranded | All | a | 0.8

## table3
Table 3
Values of relative permittivity and loss factors for the insulation of high-voltage and medium-voltage cables at power frequency
1 |  | 2 | 3
Type of cable |  | E | Tan d
Cables insulated with impregnated paper | Solid type, fully-impreganted, pre-impregnated or mass-impreganted non-draining | 3 | 0.01
| Oil filled, self contained up to Uo = 36kV | 3.6 | 0.0035
| Oil filled, self contained up to Uo = 87kV | 3.6 | 0.0033
| Oil filled, self contained up to Uo = 160kV | 3.5 | 0.003
| Oil filled, self contained up to Uo = 220kV | 3.5 | 0.002
| Oil-pressure, pipe-type | 3.7 | 0.0045
| External gas-pressure | 3.6 | 0.004
| Internal gas-pressure | 3.4 | 0.0045
Cable with other kinds of insulation | Butyle rubber | 4 | 0.05
| EPR up to and including 18/30 (36) kV cables | 3 | 0.02
| EPR greater than 18/30 (36) kV cables | 3 | 0.005
| PVC | 8 | 0.1
| PE (HD and LD) | 2.3 | 0.001
| XLPE up to and including 18/30 (36) kV cables (unfilled) | 2.5 | 0.004
| XLPE greater than 18/30 (36) kV cables (unfilled) | 2.5 | 0.001
| XLPE greater than 18/30 (36) kV cables (filled) | 3 | 0.005
| PPL equal to, or greater than 63/110 kV cables | 2.8 | 0.0014

## table4
Table 4
Absorbtion coefficient of solar radiation for cable surfaces
Material | Theta
Bitumen/Jute serving | 0.8
Polychloroprene | 0.8
PVC | 0.8
PE | 0.4
Lead | 0.6